## DATAsql_CABLES_Olex_1C_Al_X90_1
CircuitType | ConductorType | Cores | InstallType | ActiveSize | UNENCLOSED_SPACED | UNENCLOSED_SURFACE | UNENCLOSED_TOUCHING | ENCLOSED_CONDUIT | ENCLOSED_PARTIAL | ENCLOSED_COMPLETE | BURIED_DIRECT | DUCTS_SINGLE | DUCTS_PER_CABLE | NeutralSize | EarthSize | CCC | MVAM | SizeUnits | CableDetails_Insulation, | CableDetails_Sheath, | CableDetails_Screen, | CableDetails_VoltRating, | CableDetails_IsFlex, | CableDetails_Armoured, | CableDetails_ROhmsPerKM, | CableDetails_XOhmsPerKM, | CableDetails_ZOhmsPerKM, | CableDetails_ReferenceTemp, | CableDetails_MaxConductorTemp, | CableDetails_Manufacturer
SINGLE | AL | 1C | UNENCLOSED_SPACED | 25 | 117 | 112 | 91 | 87 | 70 | 45 | 139 | 102 | 114 | 0 | 0 | 117 | 3.08 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 35 | 144 | 137 | 111 | 105 | 84 | 56 | 167 | 122 | 136 | 0 | 0 | 144 | 2.24 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 50 | 177 | 167 | 136 | 129 | 103 | 0 | 198 | 147 | 164 | 0 | 0 | 177 | 1.65 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 70 | 226 | 212 | 174 | 159 | 127 | 0 | 243 | 181 | 200 | 0 | 0 | 226 | 1.15 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 95 | 280 | 262 | 216 | 198 | 158 | 0 | 291 | 221 | 239 | 0 | 0 | 280 | 0.84 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 120 | 328 | 305 | 253 | 226 | 181 | 0 | 332 | 252 | 278 | 0 | 0 | 328 | 0.672 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 150 | 377 | 350 | 291 | 255 | 204 | 0 | 372 | 283 | 311 | 0 | 0 | 377 | 0.557 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 185 | 439 | 406 | 340 | 301 | 241 | 0 | 423 | 329 | 359 | 0 | 0 | 439 | 0.455 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 240 | 527 | 485 | 408 | 360 | 288 | 0 | 492 | 388 | 417 | 0 | 0 | 527 | 0.363 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 300 | 612 | 562 | 473 | 0 | 0 | 0 | 556 | 440 | 482 | 0 | 0 | 612 | 0.307 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 400 | 723 | 660 | 559 | 0 | 0 | 0 | 638 | 516 | 553 | 0 | 0 | 723 | 0.261 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 500 | 850 | 772 | 656 | 0 | 0 | 0 | 729 | 590 | 632 | 0 | 0 | 850 | 0.228 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SPACED | 630 | 1003 | 904 | 772 | 0 | 0 | 0 | 833 | 695 | 740 | 0 | 0 | 1003 | 0.204 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 25 | [9 empty] | 0 | 0 | 112 | 3.08 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 35 | [9 empty] | 0 | 0 | 137 | 2.24 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 50 | [9 empty] | 0 | 0 | 167 | 1.65 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 70 | [9 empty] | 0 | 0 | 212 | 1.15 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 95 | [9 empty] | 0 | 0 | 262 | 0.84 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 120 | [9 empty] | 0 | 0 | 305 | 0.672 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 150 | [9 empty] | 0 | 0 | 350 | 0.557 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 185 | [9 empty] | 0 | 0 | 406 | 0.455 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 240 | [9 empty] | 0 | 0 | 485 | 0.363 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 300 | [9 empty] | 0 | 0 | 562 | 0.307 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 400 | [9 empty] | 0 | 0 | 660 | 0.261 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 500 | [9 empty] | 0 | 0 | 772 | 0.228 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_SURFACE | 630 | [9 empty] | 0 | 0 | 904 | 0.204 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 25 | [9 empty] | 0 | 0 | 91 | 3.08 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 35 | [9 empty] | 0 | 0 | 111 | 2.24 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 50 | [9 empty] | 0 | 0 | 136 | 1.65 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 70 | [9 empty] | 0 | 0 | 174 | 1.15 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 95 | [9 empty] | 0 | 0 | 216 | 0.84 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 120 | [9 empty] | 0 | 0 | 253 | 0.672 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 150 | [9 empty] | 0 | 0 | 291 | 0.557 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 185 | [9 empty] | 0 | 0 | 340 | 0.455 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 240 | [9 empty] | 0 | 0 | 408 | 0.363 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 300 | [9 empty] | 0 | 0 | 473 | 0.307 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 400 | [9 empty] | 0 | 0 | 559 | 0.261 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 500 | [9 empty] | 0 | 0 | 656 | 0.228 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | UNENCLOSED_TOUCHING | 630 | [9 empty] | 0 | 0 | 772 | 0.204 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 25 | [9 empty] | 0 | 0 | 87 | 3.08 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 35 | [9 empty] | 0 | 0 | 105 | 2.24 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 50 | [9 empty] | 0 | 0 | 129 | 1.65 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 70 | [9 empty] | 0 | 0 | 159 | 1.15 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 95 | [9 empty] | 0 | 0 | 198 | 0.84 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 120 | [9 empty] | 0 | 0 | 226 | 0.672 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 150 | [9 empty] | 0 | 0 | 255 | 0.557 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 185 | [9 empty] | 0 | 0 | 301 | 0.455 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 240 | [9 empty] | 0 | 0 | 360 | 0.363 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 300 | [9 empty] | 0 | 0 | 0 | 0.307 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 400 | [9 empty] | 0 | 0 | 0 | 0.261 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 500 | [9 empty] | 0 | 0 | 0 | 0.228 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_CONDUIT | 630 | [9 empty] | 0 | 0 | 0 | 0.204 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 25 | [9 empty] | 0 | 0 | 70 | 3.08 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 35 | [9 empty] | 0 | 0 | 84 | 2.24 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 50 | [9 empty] | 0 | 0 | 103 | 1.65 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 70 | [9 empty] | 0 | 0 | 127 | 1.15 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 95 | [9 empty] | 0 | 0 | 158 | 0.84 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 120 | [9 empty] | 0 | 0 | 181 | 0.672 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 150 | [9 empty] | 0 | 0 | 204 | 0.557 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 185 | [9 empty] | 0 | 0 | 241 | 0.455 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 240 | [9 empty] | 0 | 0 | 288 | 0.363 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 300 | [9 empty] | 0 | 0 | 0 | 0.307 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 400 | [9 empty] | 0 | 0 | 0 | 0.261 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 500 | [9 empty] | 0 | 0 | 0 | 0.228 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_PARTIAL | 630 | [9 empty] | 0 | 0 | 0 | 0.204 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 25 | [9 empty] | 0 | 0 | 45 | 3.08 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 35 | [9 empty] | 0 | 0 | 56 | 2.24 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 50 | [9 empty] | 0 | 0 | 0 | 1.65 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 70 | [9 empty] | 0 | 0 | 0 | 1.15 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
NGLE | AL | 1C | ENCLOSED_COMPLETE | 95 | [9 empty] | 0 | 0 | 0 | 0.84 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 120 | [9 empty] | 0 | 0 | 0 | 0.672 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 150 | [9 empty] | 0 | 0 | 0 | 0.557 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 185 | [9 empty] | 0 | 0 | 0 | 0.455 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 240 | [9 empty] | 0 | 0 | 0 | 0.363 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 300 | [9 empty] | 0 | 0 | 0 | 0.307 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 400 | [9 empty] | 0 | 0 | 0 | 0.261 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 500 | [9 empty] | 0 | 0 | 0 | 0.228 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | ENCLOSED_COMPLETE | 630 | [9 empty] | 0 | 0 | 0 | 0.204 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 40 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 25 | [9 empty] | 0 | 0 | 139 | 3.08 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 35 | [9 empty] | 0 | 0 | 167 | 2.24 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 50 | [9 empty] | 0 | 0 | 198 | 1.65 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 70 | [9 empty] | 0 | 0 | 243 | 1.15 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 95 | [9 empty] | 0 | 0 | 291 | 0.84 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 120 | [9 empty] | 0 | 0 | 332 | 0.672 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 150 | [9 empty] | 0 | 0 | 372 | 0.557 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 185 | [9 empty] | 0 | 0 | 423 | 0.455 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 240 | [9 empty] | 0 | 0 | 492 | 0.363 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 300 | [9 empty] | 0 | 0 | 556 | 0.307 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 400 | [9 empty] | 0 | 0 | 638 | 0.261 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 500 | [9 empty] | 0 | 0 | 729 | 0.228 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | BURIED_DIRECT | 630 | [9 empty] | 0 | 0 | 833 | 0.204 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 25 | [9 empty] | 0 | 0 | 102 | 3.08 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 35 | [9 empty] | 0 | 0 | 122 | 2.24 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 50 | [9 empty] | 0 | 0 | 147 | 1.65 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 70 | [9 empty] | 0 | 0 | 181 | 1.15 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 95 | [9 empty] | 0 | 0 | 221 | 0.84 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 120 | [9 empty] | 0 | 0 | 252 | 0.672 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 150 | [9 empty] | 0 | 0 | 283 | 0.557 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 185 | [9 empty] | 0 | 0 | 329 | 0.455 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 240 | [9 empty] | 0 | 0 | 388 | 0.363 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 300 | [9 empty] | 0 | 0 | 440 | 0.307 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 400 | [9 empty] | 0 | 0 | 516 | 0.261 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 500 | [9 empty] | 0 | 0 | 590 | 0.228 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_SINGLE | 630 | [9 empty] | 0 | 0 | 695 | 0.204 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 25 | [9 empty] | 0 | 0 | 114 | 3.08 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 35 | [9 empty] | 0 | 0 | 136 | 2.24 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 50 | [9 empty] | 0 | 0 | 164 | 1.65 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 70 | [9 empty] | 0 | 0 | 200 | 1.15 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 95 | [9 empty] | 0 | 0 | 239 | 0.84 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 120 | [9 empty] | 0 | 0 | 278 | 0.672 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 150 | [9 empty] | 0 | 0 | 311 | 0.557 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 185 | [9 empty] | 0 | 0 | 359 | 0.455 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 240 | [9 empty] | 0 | 0 | 417 | 0.363 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 300 | [9 empty] | 0 | 0 | 482 | 0.307 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 400 | [9 empty] | 0 | 0 | 553 | 0.261 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 500 | [9 empty] | 0 | 0 | 632 | 0.228 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX
SINGLE | AL | 1C | DUCTS_PER_CABLE | 630 | [9 empty] | 0 | 0 | 740 | 0.204 | MM2 | X-90 | PVC | FALSE | 0.6/1kV | FALSE | FALSE | 0 | 0 | 0 | 25 | 90 | OLEX